## Table 1 1
Project Name:
Project Address:
Date
Prepared by:
LFRA required hazardous materials submittal information
TABLE 5003.1.1 (1) 2024 INTERNATIONAL FIRE CODE
MAXIMUM ALLOWABLE QUANTITY FOR CONTROL AREA OF HAZARDOUS MATERIALS POSING A PHYISICAL HAZARD (INDOOR) a, j, m, n, p
Material |  | Class | Group when Maximum Allowable Quantity (MAQ) is exceeded | Storage b |  |  |  |  | Use‐Closed Systems b |  |  |  |  | Use‐Open Systems b
|  |  |  | Solid Pounds (cubic feet) | Liquid Gallons (pounds) | Gas (cubic feet at NTP) | Actual Quantity (pounds) | Exceeds MAQ (YES/NO) | Solid Pounds (cubic feet) | Liquid Gallons (pounds) | Gas (cubic feet at NTP) | Actual Quantity | Exceeds MAQ (YES/NO) | Solid Pounds (cubic feet) | Liquid Gallons (pounds) | Actual Quantity | Exceeds MAQ (YES/NO)
Combustible Dust |  | N/A | H‐2 | See note p | N/A | N/A |  |  | See note p | N/A | N/A |  |  | See note p | N/A
Combustible Fiber |  | Loose | H‐3 | -100 | N/A | N/A |  |  | -100 | N/A | N/A |  |  | -20 | N/A
|  | Baled |  | -1000 |  |  |  |  | -1000 |  |  |  |  | -200
Combustible Liquidq |  | II | H-2 or H-3 | N/A | 120d, e | N/A |  |  | N/A | 120d | N/A |  |  | N/A | 30d
|  | IIIA | H-2 or H-3 |  | 330d ,e |  |  |  |  | 330d |  |  |  |  | 80d
|  | IIIB | N/A |  | 13,200e, f |  |  |  |  | 13,200f |  |  |  |  | 3,300d
Cryogenics, flammable |  | N/A | H‐2 | N/A | 45d | N/A |  |  | N/A | 45d | N/A |  |  | N/A | 10d
Cryogenics, Inert |  | N/A | N/A | N/A | N/A | NL |  |  | N/A | N/A | NL |  |  | N/A | N/A
Cryogenics, oxidixing |  | N/A | H‐3 | N/A | 45d | N/A |  |  | N/A | 45d | N/A |  |  | N/A | 10d
Explosives |  | Division 1.1 | H‐1 | 1e, g | (1)e, g | N/A |  |  | 0.25g | (0.25)g | N/A |  |  | 0.25g | (0.25)g
|  | Division 1.2 | H‐1 | 1e, g | (1)e, g | N/A |  |  | 0.25g | (0.25) g | N/A |  |  | 0.25g | (0.25) g
|  | Division 1.3 | H‐1 or H‐2 | 5e, g | (5)e, g | N/A |  |  | 1g | (1) g | N/A |  |  | 1g | (1) g
|  | Division 1.4 | H‐3 | 50e, g | (50)e, g | N/A |  |  | 50g | (50)g | N/A |  |  | N/A | N/A
|  | Division 1.4G | H‐3 | 125e, k | N/A | N/A |  |  | N/A | N/A | N/A |  |  | N/A | N/A
|  | Division 1.5 | H‐1 | 1e, g | (1)e, g | N/A |  |  | 0.25g | (0.25) g | N/A |  |  | 0.25g | (0.25) g
|  | Division 1.6 | H‐1 | 1e, g | N/A | N/A |  |  | N/A | N/A | N/A |  |  | N/A | N/A
Flammable Gas |  | Gaseous | H‐2 | N/A | N/A |  |  |  | N/A | N/A |  |  |  | N/A | N/A
|  | 1A and 1B (High BV)q |  |  |  | 1,000d, e |  |  |  |  | 1,000d, e
|  | 1B (Low BV)q |  |  |  | 162,500d, e |  |  |  |  | 162,500d, e
|  | Liquefied |  |  |  | N/A |  |  |  |  | N/A
|  | 1A and 1B (High BV)q |  |  | (150)d, e |  |  |  |  | (150)d, e
|  | 1B (Low BV)q |  |  | (10,000)d, e |  |  |  |  | (10,000)d, e
Flammable Liquidc |  | 1A | H‐2 or H‐3 | N/A | 30d, e | N/A |  |  | N/A | 30d | N/A |  |  | N/A | 10d
|  | 1B and 1C |  |  | 120d, e |  |  |  |  | 120d |  |  |  |  | 30d
Flammable Liquid, combination (1A, 1B, 1C) |  | N/A | H‐2 or H‐3 | N/A | 120d, e, h | N/A |  |  | N/A | 120d, h | N/A |  |  | N/A | 30d, h
Flammable Solid |  | N/A | H‐3 | 125d, e | N/A | N/A |  |  | 125d | N/A | N/A |  |  | 25d | N/A
Inert Gas |  | Gaseous | N/A | N/A | N/A | NL |  |  | N/A | N/A | NL |  |  | N/A | N/A
|  | Liquified | N/A | N/A | N/A | NL |  |  | N/A | N/A | NL |  |  | N/A | N/A
Organic Peroxide |  | UD | H‐1 | 1e, g | (1)e, g | N/A |  |  | 0.25g | (0.25)g | N/A |  |  | 0.25g | (0.25)g
|  | I | H‐2 | 5d, e | (5)d, e | N/A |  |  | 1d | (1)d | N/A |  |  | 1d | (1)d
|  | II | H‐3 | 50d, e | (50)d, e | N/A |  |  | 50d | (50)d | N/A |  |  | 10d | (10)d
|  | III | H‐3 | 125d, e | (125)d, e | N/A |  |  | 125d | (125)d | N/A |  |  | 25d | (25)d
|  | IV | N/A | NL | NL | N/A |  |  | NL | NL | N/A |  |  | NL | NL
|  | V | N/A | NL | NL | N/A |  |  | NL | NL | N/A |  |  | NL | NL
Oxidizer |  | 4 | H‐1 | 1g | (1)e, g | N/A |  |  | 0.25g | (0.25)g | N/A |  |  | 0.25g | (0.25)g
|  | 3j | H‐2 or H‐3 | 10d, e | (10)d, e | N/A |  |  | 2d | (2)d | N/A |  |  | 2d | (2)d
|  | 2 | H‐3 | 250d, e | (250)d, e | N/A |  |  | 250d | (250)d | N/A |  |  | 50d | (50)d
|  | 1 | N/A | 4,000e, f | (4,000)e, f | N/A |  |  | 4,000f | (4,000)f | N/A |  |  | 1,000f | (1,000)f
Oxidizing Gas |  | Gaseous | H‐3 | N/A | N/A | 1500d, e |  |  | N/A | N/A | 1,500d, e |  |  | N/A | N/A
|  | Liquified |  | N/A | (150)d, e | N/A |  |  | N/A | (150)d, e | N/A |  |  | N/A | N/A
Pyrophoric Material |  | N/A | H‐2 | 4e, g | (4)e, g | 50e, g |  |  | 1g | (1)g | 10e, g |  |  | 0 | 0
Unstable (Reactive) |  | 4 | H‐1 | 1e, g | (1)e, g | 10e, g |  |  | 0.25g | (0.25)g | 2e, g |  |  | 0.25g | (0.25)g
|  | 3 | H‐1 or H‐2 | 5d, e | (5)d, e | 50d, e |  |  | 1d | (1)d | 10d, e |  |  | 1d | (1)d
|  | 2 | H‐3 | 50d, e | (50)d, e | 750d,e |  |  | 50d | (50)d | 750d,e |  |  | 10d | (10)d
|  | 1 | N/A | NL | NL | NL |  |  | NL | NL | NL |  |  | NL | NL
Water Reactive |  | 3 | H‐2 | 5d, e | (5)d, e | N/A |  |  | 5d | (5)d | N/A |  |  | 1d | (1)d
|  | 2 | H‐3 | 50d, e | (50)d, e | N/A |  |  | 50d | (50)d | N/A |  |  | 10d | (10)d
|  | 1 | N/A | NL | NL | N/A |  |  | NL | NL | N/A |  |  | NL | NL
For SI: 1 cubic foot = 0.02832 m3 , 1 pound = 0.454 kg, 1 gallon = 3.785 L.
NA = Not Applicable, NL = Not Limited, UD = Unclassified Detonable.
a. | For use of control areas, see Section 5003.8.3.
b. | The aggregate quantity in use and storage shall not exceed the quantity listed for storage, including applicable increases.
c. | For hazardous materials in Group B higher education laboratory occupancies, see Section 428 of the International Building Code and Chapter 38.
d. | Maximum allowable quantities shall be increased 100 percent in buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. Where Note e also applies, the increase for both notes shall be applied accumulatively.
e. | Maximum allowable quantities shall be increased 100 percent where stored in approved storage cabinets, day boxes, gas cabinets, gas rooms, exhausted enclosures, or in listed safety cans in accordance with Section 5003.9.10. Where Note d also applies, the increase for both notes shall be applied accumulatively.
f. | Quantities shall not be limited in a building equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.
g. | Allowed only in buildings equipped throughout with an approved automatic sprinkler system.
h. | Containing not more than the maximum allowable quantity per control area of Class 1A, Class 1B, or Class 1C flammable liquids.
i. | Quantities in parentheses indicate quantity units in parentheses at the head of each column.
j. | A maximum quantity of 220 pounds of solid or 22 gallons of liquid Class 3 oxidizers is allowed where such materials are necessary for maintenance purposes, operation or sanitation of equipment where the storage containers and the manner of storage are approved.
k. | Net weight of pyrotechnic composition of the fireworks. Where the net weight of the pyrotechnic composition of the fireworks is not known, 25 percent of the gross weight of the fireworks including packaging shall be used.
l. | For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 5003.1.2.
m. | For oxidizers, unstable (reactive) materials and water-reactive materials stored or displayed in Group M occupancies or stored in Group S occupancies, see Section 5003.11.
n. | For flammable and combustible liquid storage in Group M occupancy wholesale and retail sales uses, see Section 5704.3.6.
o. | Quantities in this table shall be modified in accordance with Table 5003.1.1(5).
p. | Where manufactured, generated or used in such a manner that the concentration and conditions create a fire or explosion hazard based on information prepared in accordance with Section 104.8.2.
q. | "High BV" Category 1B flammable gas has a burning velocity greater than 3.9 in/s (10 cm/s). "Low BV" Category 1B flammable gas has a burning velocity of 3.9 in/s or less.

## Table 2 1
Project Name:
Project Address:
Date
Prepared by:
LFRA required hazardous materials submittal information
TABLE 5003.1.1(2) 2024 INTERNATIONAL FIRE CODE
MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIAL POSING A HEALTH HAZARD (INDOOR) a, c, f, h, i
Material |  | Storage b |  |  |  |  | Use‐Closed Systems b |  |  |  |  | Use‐Open Systems b
|  | Solid Pounds d,e | Liquid Gallons (pounds) d,e | Gas cubic feet at NTP (pounds) d | Actual Quantity (pounds) | Exceeds MAQ (YES/NO) | Solid Pounds d | Liquid Gallons (pounds) d | Gas cubic feet at NTP (pounds) d | Actual Quantity (pounds) | Exceeds MAQ (YES/NO) | Solid Pounds d | Liquid Gallons (pounds) d | Actual Quantity | Exceeds MAQ (YES/NO)
Corrosives |  | 5000 | 500 | Gaseous 810 e |  |  | 5000 | 500 | Gaseous 810 e |  |  | 1000 | 100
|  |  |  | Liquified (150) |  |  |  |  | Liquified (150)
Highly Toxics |  | 10 | -10 | Gaseous 20 g |  |  | 10 | -10 | Gaseous 20 g |  |  | 3 | -3
|  |  |  | Liquified (4) g |  |  |  |  | Liquified (4) g
Toxics |  | 500 | -500 | Gaseous 810 e |  |  | 500 | -500 | Gaseous 810 e |  |  | 125 | -125
|  |  |  | Liquified (150) e |  |  |  |  | Liquified (150) e
For SI: 1 cubic foot = 0.02832 m3 , 1 pound = 0.454 kg, 1 gallon = 3.785 L.
a. | For use of control areas, see Section 5003.8.3.
b. | The aggregate quantity in use and storage shall not exceed the quantity listed for storage.
c. | In retail and wholesale sales occupancies, the quantities of medicines, foodstuff or consumer products and cosmetics, contraining not more than 50 percent by volume of water-miscible liquids and with the remainder of the solutions not being flammable, shall not be limited, provided that such materials are packaged in individual containers not exceeding 1.3 gallons.
d. | Maximum allowable quantities shall be increased 100 percent in buildings equipped throughout with an approved automatice sprinkler system in accordance with Section 903.3.1.1. Where Note e also applies, the increase for both notes shall be applied accumulatively.
e. | Maximum allowable quantities shall be increased 100 percent when stored in approved storage cabinets, gas cabinets or exhausted enclosures. Where Note d applies, the increase for both notes shall be applied accumulatively.
f. | For storage and display quantities in Group M and storage quantities in Group S occupancies complying with Section 5003.11, see Table 5003.11.1.
g. | Allowed only when stored in approved exhausted gas cabinets or exhausted enclosures.
h. | Quantities in parentheses indicate quantity units in parentheses at the head of each column.
i. | For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 5003.1.2.
j. | Quantities in this table shall be modified in accordance with Table 5003.1.1(5).

## Table 3 1
Project Name:
Project Address:
Date
Prepared by:
LFRA required hazardous materials submittal information
TABLE 5003.1.1(3) 2024 INTERNATIONAL FIRE CODE
MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIALS POSING A PHYISCAL HAZARD IN AN OUTDOOR CONTROL AREA a, b, c, d
Material |  | Class | Storage b |  |  |  |  | Use‐Closed Systems b |  |  |  |  | Use‐Open Systems b
|  |  | Solid Pounds (cubic feet) | Liquid Gallons (pounds) d | Gas (cubic feet at NTP) | Actual Quantity | Exceeds MAQ (YES/NO) | Solid Pounds (cubic feet) | Liquid Gallons (pounds) d | Gas (cubic feet at NTP) | Actual Quantity | Exceeds MAQ (YES/NO) | Solid Pounds (cubic feet) | Liquid Gallons (pounds) d | Actual Quantity | Exceeds MAQ (YES/NO)
Flammable gas |  | Gaseous | N/A | N/A |  |  |  | N/A | N/A |  |  |  | N/A | N/A
|  | 1A and 1B (High BV)E |  |  | 3000 |  |  |  |  | 1500
|  | 1B (Low BV)e |  |  | 195000 |  |  |  |  | 97500
|  | Liquefied |  |  | N/A |  |  |  |  | N/A
|  | 1A and 1B (High BV)e |  | -300 |  |  |  |  | -150
|  | 1B (low BV)e |  | -20000 |  |  |  |  | -10000
Flammable solid |  | N/A | 500 | N/A | N/A |  |  | 250 | N/A | N/A |  |  | 50 | N/A
Inert Gas |  | Gaseous | N/A | N/A | Not Limited |  |  | N/A | N/A | Not Limited |  |  | N/A | N/A
|  | Liquified | N/A | N/A | Not Limited |  |  | N/A | N/A | Not Limited |  |  | N/A | N/A
Cryogenic Inert |  | N/A | N/A | N/A | Not Limited |  |  | N/A | N/A | Not Limited |  |  | N/A | N/A
Organic peroxide |  | Unclassified Detonable | 1 | -1 | N/A |  |  | 0.25 | -0.25 | N/A |  |  | 0.25 | -0.25
Organic peroxide |  | I | 20 | -20 | N/A |  |  | 10 | -10 | N/A |  |  | 2 | -2
|  | II | 200 | -200 |  |  |  | 100 | -100 |  |  |  | 20 | -20
|  | III | 500 | -500 |  |  |  | 250 | -250 |  |  |  | 50 | -50
|  | IV | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited
|  | V | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited
Oxidizer |  | 4 | 2 | -2 | N/A |  |  | 1 | -1 | N/A |  |  | 0.25 | -0.25
|  | 3 | 40 | -40 |  |  |  | 20 | -20 |  |  |  | 4 | -4
|  | 2 | 1000 | -1000 |  |  |  | 500 | -500 |  |  |  | 100 | -100
|  | 1 | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited
Oxidizing gas |  | Gaseous | N/A | N/A | 6000 |  |  | N/A | N/A | 1500 |  |  | N/A | N/A
|  | Liquified |  | -600 | N/A |  |  |  | -300 | N/A
Pyrophoric materials |  | N/A | 8 | -8 | 100 |  |  | 4 | -4 | 10 |  |  | 0 | 0
Unstable (reactive) |  | 4 | 2 | -2 | 20 |  |  | 1 | -1 | 2 |  |  | 0.25 | -0.25
|  | 3 | 20 | -20 | 200 |  |  | 10 | -10 | 10 |  |  | 1 | 1
|  | 2 | 200 | -200 | 1000 |  |  | 100 | -100 | 250 |  |  | 10 | 10
|  | 1 | Not Limited | Not Limited | Not Limited |  |  | Not Limited | Not Limited | Not Limited |  |  | Not Limited | Not Limited
Water reactive |  | 3 | 20 | -20 | N/A |  |  | 10 | -10 | N/A |  |  | 1 | -1
|  | 2 | 200 | -200 |  |  |  | 100 | -100 |  |  |  | 10 | -10
|  | 1 | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited |  |  |  | Not Limited | Not Limited
For SI: 1 pound = 0.454 kg, 1 gallon = 3.785 L., 1 cubic foot = 0.02832 m3.
a. | For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 5003.1.2.
b. | The aggregate quantities in storage and use shall not exceed the maximum allowable quantity for storage, including applicable increases.
c. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials allowed in outdoor storage per single property under the same ownership or control used for retail or wholesale sales is allowed to exceed the maximum allowable quantity per control area where such storage is in accordance with Section 5003.11.
d. | Quantities in parentheses indicate quantity units in parentheses at the head of each column.
e. | "High BV" Category 1B flammable gas has a burning velocity greater than 3.9 in/s (10 cm/s). "Low BV" Category 1B flammable gas has a burning velocity of 3.9 in/s or less.

## Table 4 1
Project Name:
Project Address:
Date
Prepared by:
LFRA required hazardous materials submittal information
TABLE 5003.1.1(4) 2024 INTERNATIONAL FIRE CODE
MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIAL POSING A HEALTH HAZARD IN AN OUTDOOR CONTROL AREA a, b, c, f
Material |  | Storage |  |  |  |  | Use‐Closed Systems |  |  |  |  | Use‐Open Systems
|  | Solid Pounds | Liquid Gallons (pounds) | Gas cubic feet at NTP (pounds) | Actual Quantity | Exceeds MAQ (YES/NO) | Solid Pounds | Liquid Gallons (pounds) | Gas cubic feet at NTP (pounds) | Actual Quantity | Exceeds MAQ (YES/NO) | Solid Pounds | Liquid Gallons (pounds) | Actual Quantity | Exceeds MAQ (YES/NO)
Corrosives |  | 20000 | 2000 | Gaseous 1,620 |  |  | 10000 | 1000 | Gaseous 810 |  |  | 1000 | 100
|  |  |  | Liquified (300) |  |  |  |  | Liquified (150)
Highly Toxics |  | 20 | -20 | Gaseous 40 d |  |  | 10 | -10 | Gaseous 20 d |  |  | 3 | -3
|  |  |  | Liquified (8) d |  |  |  |  | Liquified (4)d
Toxics |  | 1000 | (1,000) e | Gaseous 1,620 |  |  | 500 | 50 e | Gaseous 810 |  |  | 125 | (125) e
|  |  |  | Liquified (300) |  |  |  |  | Liquified (150)
For SI: 1 cubic foot = 0.02832 m3 , 1 pound = 0.454 kg, 1 gallon = 3.785 L., 1 pound per square inch absolute = 6.895 kPa, oCelcius = (oFarenheit- 32)/1.8].
a. | For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 5003.1.2.
b. | The aggregate quantities in storage and use shall not exceed the quantity listed for storage, including applicable increases.
c. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials allowed in outdoor storage per single property under the same ownership or control used for retail or wholesale sales is allowed to exceed the maximum allowable quantity per control area where such storage is in accordance with Section 5003.11.
d. | Allowed only where used in approved exhausted gas cabinets, exhausted enclosures or under fume hoods.
e. | The maximum allowable quantity per control area for toxic liquids with vapor pressures in excess of 1 psia at 77oF shall be the maximum allowable quantity per control area listed for highly toxic liquids.
f. | Quantities in parentheses indicate quantity units in parentheses at the head of each column.